- Petition - 199 IAC 11.8(1)

- Extension petition form on IUC website

- Show the docket number, Iowa Code version, company name and address, county, and the length and maximum voltage of the line

- Show the contact information if a map was requested

- Petition must be signed

- Affidavit must be signed and notarized

Common errors:

- Incorrect version of Iowa Code

- Incorrect distance of line route

- Not designating which map is available to the public

- Notary Commission has expired

- Signatures not redacted

- Exhibit A - 199 IAC 11.8(1)(a)

- Refer to example on IUC website for expected format

- Name of the county

- Nominal and maximum voltages are given

- Beginning and ending points of the line

- Right-of-way type (public, private, railroad) for every segment is provided

- Termini locations

  - A terminus must be a substation, three-way switch pole, generating station, or other electric line that the proposed line will tap to it

- Termini in other counties, if applicable

- Description should be consistent with Exhibit B

- Section, township, and range information provided for each segment, including crossing or in or adjacent to the right-of-way of a named road and/or named railroad

- Identify all counties involved in the project

- Last sentence details total mileage

- Page numbers needed for Exhibit A

- For multiple segments:

  - Last sentence of each segment details the total mileage

  - Sum of segments is the same as the mileage requested on the petition

Common errors:

- Voltage needs to be included

- Legal description accurate (miles shown in two decimal points)

- Designate private or public right-of-way

- Mileage of Exhibit A does not match mileage of petition

- No page number if more than one page

- Exhibit B - 199 IAC 11.8(1)(b)

- Refer to example on IUC website

- Entire route of the line as described in Exhibit A

- Scale not less than one inch per mile on an 11” x 17” sheet

- Legend with all symbols and acronyms defined and compass (north specified)

- Starting and ending points of the line

- For lines that parallel road or railroad, clearly shows which side the line is on

- Sections with double circuit or underbuild are clearly indicated and understandable

- Line symbols used to clearly indicate nominal voltage and ownership of all electric lines either as multiple-circuit construction or underbuild on the subject line on the map

- Consistent with Iowa Department of Transportation (IDOT) county maps (available on the IDOT website) and Iowa Sportsman’s Atlas (if applicable)

- General requirements for map:

  - County names and boundaries (if applicable)

  - Name and corporate limits of cities

  - Section, township, and range information: lines, numbers, and boundaries

  - Location, owner name, and address of railroads

  - Significant features or landmarks are shown

- Sheet numbers are correct

- Buildings and grain bins with clearance drawings in Exhibit C shown on map

- Electric transmission lines that the cross the route shown on map

Common errors:

- Not identifying all existing electric lines

- Inaccurate or out-of-date contact addresses

- Not showing everything; i.e., cemetery

- Scale not appropriate

- Line symbols not being consistent

- Symbols not being defined in the legend

- Voltage and/or mileage not consistent with either the petition or other exhibits

- Not indicating whether an existing line is to be removed and/or rebuilt

- Not reviewing digital files for legibility before submitting

- Corporate and/or city limits not consistent with IDOT or county assessor maps

- Exhibit C - 199 IAC 11.8(1)(c)

See Exhibit C Instructions for more details

- Length and location of the segment must be consistent with Exhibits A and B

- Correct section, township, and range information for each segment

- Indicate the correct maximum and nominal voltage for each segment

- Indicate clearances as required by the appropriate NESC edition

- Correct phase conductor information

- Correct insulator type and flashover voltage ratings

- Information for second transmission line or underbuild circuit, if applicable

- Total length indicated in Exhibit C segments should be consistent with Exhibits A and B and the Petition

- Structure drawings need to show:

  - Dimensions consistent with the Exhibit C

  - Insulator length

  - Vertical and horizontal lengths between phase conductors

  - Vertical and horizontal lengths between conductors of different circuits

  - Vertical and horizontal lengths between top phase conductor and shield wire

  - Underbuild circuit, if applicable

- Grain bin, angle, tangent, and dead-end drawings, if applicable

- Conductor crossing clearance drawing, if the line crosses another transmission line

- Conductor clearance drawing from buildings, if building identified as less than 30 feet from line during inspection

Common errors:

- Railroad crossing requires additional three feet of clearance

- Using the correct NESC edition for required adders and additional adders

- Additional adder due to higher voltage than the NESC’s voltage omitted in grain bin clearance drawings

- Required clearance drawings missing

- Building, grain bin, or transmission line shown on Exhibit B but no clearance drawing provided

- Exhibit D - 199 IAC 11.8(1)(d)

- Existing franchise issuance date must not exceed 25 years from the date of the petition filing

- Petition for extension should be filed one year before existing franchise expiration date or have a request to waive 199 IAC 11.8(2)

- Existing franchise number, docket number, date of issue, county of location, and to whom granted

- A listing of all amendments to the franchises listed, including the docket number, amendment number, date of issue, and purpose of the amendment

- A description of any substantial rebuilds, reconstructions, alterations, relocations, or changes in operation not included in a prior franchise or amendment action

- A description of any changes in ownership or operating and maintenance responsibility

- An allegation, with supporting testimony, that the line remains necessary to serve a public use and represents a reasonable relationship to an overall plan of transmitting electricity in the public interest

- Any other information or explanations in support of the petition

- Verify previous franchise has not expired

- An explanation would be included if the petition is filed less than a year from a current expiration date

- Field Inspection - 199 IAC 11.9(4)

- Any violations will need to be addressed prior to final action taken by the IUC

- Additional corrections to exhibits and petition may be required after inspection

- Franchise Publication Notice - 199 11.8(5), 11.8(6),

- Official notice will be filed after all deficiencies in the petition and exhibits have been corrected

- Affidavit must be dated and signed after the second publication date

- Notices for one project filed in multiple dockets must be filed at the same time

- The newspaper publication dates must match the publication dates shown in the official notice (as first and second publication dates) and in the newspaper publisher’s affidavit

Rev. 3.2025